SECTION 26 51 19

LED INTERIOR LIGHTING

- PART 1 GENERAL

SECTION INCLUDES

Linear LED Lighting with Acoustical Softgrid® Modular Ceiling Panels

Remote LED Driver

RELATED SECTIONS

Section 09 54 34 - Suspended Modular Ceiling Panels

Division 23 (15) Sections – HVAC

Division 26 (16) Sections – Electrical

REFERENCES

TEST METHODS

ASTM C 423 Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method.

ASTM E 84 Standard Test Method for Surface Burning Characteristics of Building Materials.

QUALITY ASSURANCE

Manufacturer Qualifications: Primary products in this section to be provided by a manufacturer with no less than five years of experience producing the products specified in this section at a facility in the United States.

Installer's Qualifications: All work specified in this section is to be completed by a firm with demonstrated experience installing systems similar in scope and complexity to those specified.

Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.

DELIVERY, STORAGE, AND HANDLING

Store the Acoustical Softgrid® modular ceiling panels in an interior location and keep in cartons prior to installation to avoid damage.

Exercise care in moving and opening cartons to prevent damage to the panel face.

Protect from damage due to weather, excessive temperature, and construction operations.

PROJECT CONDITIONS

Within the installation space all wet work must be complete and dry prior to installation.

Installation shall be carried out where the temperature is between 40 degrees F and 90 degrees F. These temperature conditions must be maintained throughout the life of the warranty.

WARRANTY

Manufacturer’s Warranty: Manufacturer agrees to replace products that fail within the specified warranty period per product type.

Warranty Period:

Acoustic Panels: One (1) year from date of substantial completion.

Attachment devices: One (1) year from date of substantial completion.

Lighting Components and Drivers: Five (5) years from the date of substantial completion.

Warranty Language:

Manufacturers’ products are expressly warranted to be free from defects in material and workmanship, when installed according to manufacturer’s published installation procedures, for the warranty period applicable to the specific product type from date of substantial completion. During the applicable warranty period manufacturer will repair or at its option replace the products that are proven to be defective. Manufacturer is NOT responsible for any intentional or accidental abuse, misuse, or neglect incurred on the original warranted product, and shall as determined by manufacturer, void the warranty.

- PRODUCTS

MANUFACTURER

Basis Of Design Manufacturer: Arktura LLC.

Address: 966 Sandhill Ave, Carson, CA 90746

Phone: 310-532-1050

Email: info@arktura.com

Web: https://arktura.com/products/lighting/#softgrid-light

PERFORMANCE REQUIREMENTS

System Certifications:

UL/cUL and ETL certification marks for Canada/USA.

Safety Standards:

UL/cUL 2108; Pass, Low Voltage Lighting Systems

UL/cUL 8750; Pass, Standard for Light Emitting Diode (LED) Equipment for use in Lighting Products.

LINEAR LED LIGHTING INTEGRATED WITHIN ACOUSTIC PANELS

Basis of Design Product: SoftGrid® Light

Module Dimensions:

        - SoftGrid® Light Flux - 60 x 69.3125 x 5.625 Inches

        - SoftGrid® Light Sine - 90 x 90 x 7.6875 Inches

        - SoftGrid® Light Square - 90 x 90 x 7.75 Inches

        - SoftGrid® Light Switch - 90 x 90 x 7.875 Inches

        - SoftGrid® Light Wave - 90 x 90 x 11.5 Inches

Installation Method: Suspended

Installation Environment: Indoors/Dry Location

Lighting Configuration: Direct

Lighting Performance:

Power Level: 3.4W/FT, 42W/1.75A Per Module

Color Temperature (CCT): 3000K, 3500K, 4000K or Custom

Color Rendering Index (CRI): 90+

Light Output:

        - Flux, Switch, Square, Sine - 3840 lm Per Module, 320 lm/FT

        - Wave - 3432 lm Per Module, 286 lm/FT

Construction

Lens: Frosted Silicone, uninterrupted illumination without visible pixels or shadowing.

Enclosure: PET Felt, Sound Absorption and Fire Ratings per Arktura SoftSound specifications.

Power Cable(s): UL 2464 Power Cable

Suspension: Stainless Steel Cables and Adjustable Grippers

Canopy: Painted Steel 5” Round

REMOTE DRIVER

Basis of Design Product: Arktura Dimmable 288W LED Driver

Dimensions - 12 x 4.4 x 1.8 Inches

Installation Method - Surface Mount

Installation Environment: Indoor/Damp/Wet Location (Driver Only)

Dimming: 0-10V

Electrical:

        - Input Voltage: 120-277VAC

        - Input Power:

          - One Module Per Output – @120V - 54VA, @277V 54VA

          - Two Modules Per Output – @120V - 99VA, @277V 97VA

        - Output Voltage: 24VDC

        - Output Power: 288W, 3X 96W Outputs

EXECUTION

EXAMINATION

Do not begin work until adjacent substrates have been properly constructed prepared to receive work specified in this section.

PREPARATION

Clean surfaces thoroughly prior to installation.

Protect all adjacent surfaces from possible damage during installation of units.

Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

INSTALLATION

Install in accordance with manufacturer’s installation instructions, industry recognized best practices, and all code bodies having jurisdiction; do not install damaged products.

Test for proper operation and adjust until satisfactory results are obtained.

Protect fixture materials from damage during installation using manufacturer’s recommendations.

CLEANING AND PROTECTION

Clean products in accordance with the manufacturer’s recommendations.

Repair or replace damaged products before Substantial Completion.

Protect installed products until completion of work specified in this section.

- END OF SECTION