SECTION 26 51 19
LED INTERIOR LIGHTING
PART 1 GENERAL
SECTION INCLUDES
Linear LED Lighting with Acoustical Softgrid® Modular Ceiling Panels
Remote LED Driver
RELATED SECTIONS
Section 09 54 34 - Suspended Modular Ceiling Panels
Division 23 (15) Sections – HVAC
Division 26 (16) Sections – Electrical
REFERENCES
TEST METHODS
ASTM C 423 Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method.
ASTM E 84 Standard Test Method for Surface Burning Characteristics of Building Materials.
QUALITY ASSURANCE
Manufacturer Qualifications: Primary products in this section to be provided by a manufacturer with no less than five years of experience producing the products specified in this section at a facility in the United States.
Installer's Qualifications: All work specified in this section is to be completed by a firm with demonstrated experience installing systems similar in scope and complexity to those specified.
Source Limitations: Provide each type of product from a single manufacturing source to ensure uniformity.
DELIVERY, STORAGE, AND HANDLING
Store the Acoustical Softgrid® modular ceiling panels in an interior location and keep in cartons prior to installation to avoid damage.
Exercise care in moving and opening cartons to prevent damage to the panel face.
Protect from damage due to weather, excessive temperature, and construction operations.
PROJECT CONDITIONS
Within the installation space all wet work must be complete and dry prior to installation.
Installation shall be carried out where the temperature is between 40 degrees F and 90 degrees F. These temperature conditions must be maintained throughout the life of the warranty.
WARRANTY
Manufacturer’s Warranty: Manufacturer agrees to replace products that fail within the specified warranty period per product type.
Warranty Period:
Acoustic Panels: One (1) year from date of substantial completion.
Attachment devices: One (1) year from date of substantial completion.
Lighting Components and Drivers: Five (5) years from the date of substantial completion.
Warranty Language:
Manufacturers’ products are expressly warranted to be free from defects in material and workmanship, when installed according to manufacturer’s published installation procedures, for the warranty period applicable to the specific product type from date of substantial completion. During the applicable warranty period manufacturer will repair or at its option replace the products that are proven to be defective. Manufacturer is NOT responsible for any intentional or accidental abuse, misuse, or neglect incurred on the original warranted product, and shall as determined by manufacturer, void the warranty.
- PRODUCTS
MANUFACTURER
Basis Of Design Manufacturer: Arktura LLC.
Address: 966 Sandhill Ave, Carson, CA 90746
Phone: 310-532-1050
Email: info@arktura.com
Web: https://arktura.com/products/lighting/#softgrid-light
PERFORMANCE REQUIREMENTS
System Certifications:
UL/cUL and ETL certification marks for Canada/USA.
Safety Standards:
UL/cUL 2108; Pass, Low Voltage Lighting Systems
UL/cUL 8750; Pass, Standard for Light Emitting Diode (LED) Equipment for use in Lighting Products.
LINEAR LED LIGHTING INTEGRATED WITHIN ACOUSTIC PANELS
Basis of Design Product: SoftGrid® Light
Module Dimensions:
a. SoftGrid® Light Flux - 60 x 69.3125 x 5.625 Inches
b. SoftGrid® Light Sine - 90 x 90 x 7.6875 Inches
c. SoftGrid® Light Square - 90 x 90 x 7.75 Inches
d. SoftGrid® Light Switch - 90 x 90 x 7.875 Inches
e. SoftGrid® Light Wave - 90 x 90 x 11.5 Inches
Installation Method: Suspended
Installation Environment: Indoors/Dry Location
Lighting Configuration: Direct
Lighting Performance:
Power Level: 3.4W/FT, 42W/1.75A Per Module
Color Temperature (CCT): 3000K, 3500K, 4000K or Custom
Color Rendering Index (CRI): 90+
Light Output:
f. Flux, Switch, Square, Sine - 3840 lm Per Module, 320 lm/FT
g. Wave - 3432 lm Per Module, 286 lm/FT
Construction
Lens: Frosted Silicone, uninterrupted illumination without visible pixels or shadowing.
Enclosure: PET Felt, Sound Absorption and Fire Ratings per Arktura SoftSound specifications.
Power Cable(s): UL 2464 Power Cable
Suspension: Stainless Steel Cables and Adjustable Grippers
Canopy: Painted Steel 5” Round
REMOTE DRIVER
Basis of Design Product: Arktura Dimmable 288W LED Driver
Dimensions - 12 x 4.4 x 1.8 Inches
Installation Method - Surface Mount
Installation Environment: Indoor/Damp/Wet Location (Driver Only)
Dimming: 0-10V
Electrical:
h. Input Voltage: 120-277VAC
i. Input Power: 
1) One Module Per Output – @120V - 54VA, @277V 54VA
2) Two Modules Per Output – @120V - 99VA, @277V 97VA
j. Output Voltage: 24VDC
k. Output Power: 288W, 3X 96W Outputs
EXECUTION
EXAMINATION
Do not begin work until adjacent substrates have been properly constructed prepared to receive work specified in this section.
PREPARATION
Clean surfaces thoroughly prior to installation.
Protect all adjacent surfaces from possible damage during installation of units.
Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.
INSTALLATION
Install in accordance with manufacturer’s installation instructions, industry recognized best practices, and all code bodies having jurisdiction; do not install damaged products.
Test for proper operation and adjust until satisfactory results are obtained.
Protect fixture materials from damage during installation using manufacturer’s recommendations.
CLEANING AND PROTECTION
Clean products in accordance with the manufacturer’s recommendations.
Repair or replace damaged products before Substantial Completion.
Protect installed products until completion of work specified in this section.
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